## Sheet1
Location | Observation | Risk in Detail | Correction Action | Targate Date | Status
Siemens SWGR, Kalwa (Siemens Inbound) | hallways, stairwells and lobbies not kept free of trash and debris and not used for storage | Increased fire load, which can contribute to rapid fire spread. Difficulty in accessing fire-fighting equipment and emergency exits. Designate separate storage areas for materials and equipment |  | 31.07.203 | Closed
Siemens SWGR, Kalwa (Siemens Inbound) | row guards not in good condition | Reduced protection of rack uprights from forklift or MHE impacts. Increased risk of rack damage leading to structural instability Inspect all damaged row guards and replace or repair them immediately |  | 31.07.203 | Open
Siemens SWGR, Kalwa (Siemens Inbound) | Safe Working load not displayed on the HDR/MTS | Increased risk of overloading the rack/platform/system beyond its design limits Display clear and durable SWL signage at visible locations on all HDR/MTS units. |  | 31.07.203 | Open
Siemens SWGR, Kalwa (Siemens Inbound) | Fire-rated emergency exit doors with push bar (panic bar) mechanisms are not available at designated emergency exits. Also fire exit locked & blocked | Delayed evacuation during fire or other emergency situations. Employees may face difficulty opening exit doors quickly under panic conditions Ensure doors open in the direction of travel and remain unobstructed at all times. Verify fire-rating certification and compliance with applicable fire safety standards. |  | 31.07.203 | Open
Siemens SWGR, Kalwa (Siemens Inbound) | spill kit not available and pictorial chart displayed on how to use a spill kit | Delay in response to chemical, oil, or hazardous material spills. Increased risk of slips, trips, and falls due to uncontrolled spill spread. Provide an appropriate spill kit at the designated location based on the materials handled. |  | 31.07.203 | Open
Siemens SWGR, Kalwa (Siemens Inbound) | electrical rubber mats conforming to IS 15652 kept under each panel boards | no electrical matt under electrical panel & sub-stations The electrical mat must be available at all electrical stations to avoid electricution If Its Dielectivc Epoxy & certification maintained for same then no need to install. |  | 31.07.203 | Open
Siemens SWGR, Kalwa (Siemens Inbound) | each employee on walking/working surfaces protected from tripping in or stepping into | Increased likelihood of incidents during material handling or equipment movement. Repair damaged or uneven walking surfaces. Provide adequate lighting and warning signage. |  | 31.07.203 | Open
Siemens SWGR, Kalwa (Siemens Inbound) | Step ladder was damaged | Damaged product must get identified under maintanance or Not in Use. Keeping in working area may get used by coworker leading to unsafe act. |  | 31.07.203 | Closed
Siemens Thane, Kalwa (Logistics Industry) | each employee on walking/working surfaces protected from tripping in or stepping into | Increased likelihood of incidents during material handling or equipment movement. Repair damaged or uneven walking surfaces. Provide adequate lighting and warning signage. |  |  | Open
Siemens Thane, Kalwa (Logistics Industry) | Cutting saw machine in the logistics area does not have a Safety Work Instruction (SWI) / operating procedure displayed at the point of use. | Operators may be unaware of the correct operating procedure and safety precautions Display a clear Safety Work Instruction (SWI) at the cutting saw machine. Include operating steps, emergency stop procedures, hazard warnings, and mandatory PPE requirements in the instruction. Verify that all operators are trained and authorized to use the equipment |  |  | Open
Siemens Thane, Kalwa (Logistics Industry) | AMTC Logistic area -Crane hook hanging above head | Mark the area and restrict access if the hook must remain at a lower level temporarily. Train crane operators on proper crane shutdown and hook parking procedures. |  | 20.06.26 | Closed
Siemens Thane, Kalwa (Logistics Industry) | In the AMTC Logistics staging area, no dedicated walking aisle has been provided for personnel movement and emergency exit access. The area is obstructed by staged materials. | Obstruction of emergency evacuation routes, delaying personnel escape during emergencies. Increased risk of slips, trips, and falls while navigating around stored materials. Establish and clearly mark dedicated pedestrian walkways and emergency exit aisles within the staging area. |  |  | Open
Siemens Thane, Kalwa (Switch-Board) | hallways, stairwells and lobbies kept free of trash and debris and not used for storage | Increased fire load, which can contribute to rapid fire spread. Difficulty in accessing fire-fighting equipment and emergency exits. Designate separate storage areas for materials and equipment
Siemens Thane, Kalwa (Switch-Board) | Are electrical rubber mats conforming to IS 15652 kept under each panel boards ? | no electrical matt under electrical panel & sub-stations The electrical mat must be available at all electrical stations to avoid electricution If Its Dielectivc Epoxy & certification maintained for same then no need to install.
Siemens Thane, Kalwa (Switch-Board) | No fire detection system & fire exit Locked & blocked | Fire detection system is not available at WSWB outsourcing area SD not available under CT mazzanine rack for MTS storage fire Exits are blocked in both switch gear & switch Board wih Material
Siemens Thane, Kalwa (Switch-Board) | Lifting belts/slings found torned or not maintained in the switchboard/electrical panel area. | Damaged lifting belts/slings may fail during lifting operations, leading to dropped loads. Risk of serious injury or fatality to personnel from falling materials Train employees on lifting gear inspection, storage, and rejection criteria. Use sling cover to protect from tearing & belt damage.
Siemens Thane, Kalwa (Switch-Board) | Fire-rated emergency exit doors with push bar (panic bar) mechanisms are not available at designated emergency exits. | Delayed evacuation during fire or other emergency situations. Employees may face difficulty opening exit doors quickly under panic conditions Ensure doors open in the direction of travel and remain unobstructed at all times. Verify fire-rating certification and compliance with applicable fire safety standards.
Siemens Thane, Kalwa (Switch-Board) | Fire detection system is not available at WSWB outsourcing area SD not available under CT mazzanine rack for MTS storage | Install an appropriate fire detection system (smoke/heat detectors) covering the entire outsourcing area. Integrate the detection system with the site's fire alarm panel.